## Sheet1
Number | Topic | Question | Answer
1 | Implementation Phase | The Implementation Phase placeholder pricing assumes that all radios are upgraded to the latest MDS Orbit model. Does Thornton anticipate approving full replacement at all sites, or does Thornton expect a mix of replacement, repair, and reconfiguration? | This will ultimately be determined during the Recommendation Phase, but Thornton anticipates that it will replace radios at all sites to standardize the radios in use, contingent on available budget.
2 | Implementation Phase | The Implementation Phase placeholder pricing assumes that all radios are upgraded to the latest MDS Orbit model. Will unit pricing per radio govern final Implementation pricing once recommendations are accepted? | Radio unit pricing in vendor proposals is not binding on the Implementation Phase, as the price for Implementation will be re-negotiated during contract performance. Once recommendations are accepted and the price for Implementation is agreed upon, the amount for Implementation (line 2 on the Pricing Form) will be firm and fixed. The price will be fixed at the line item level - that is, for Implementation as a whole, tasks 7 through 11 - but not at the various components that make up that price, like the unit cost of radios.
3 | Fiber conversion | Are there any remote sites planned for near-term fiber conversion where radios may be retired rather than replaced? | No, not at this time.
4 | Repeater locations | For the three repeater locations, are any civil, structural, electrical, grounding, or antenna tower modifications anticipated beyond radio-related equipment replacement? | The Wes Brown Repeater site antenna and cable will most likely need to be replaced. The other two sites are in good condition.
5 | Repeater locations | For the three repeater locations, can Thornton confirm that the scope is limited to radio, cabling, antenna, and lightning protection components only? | For all locations - the three repeater sites and all remote sites - the scope includes not only the radios but also the radio-related infrastructure, including radio enclosures, grounding/lightning protection, antennas, cabling, and mounts. See Addendum No. 1 to the RFP. Thornton anticipates that most of these existing components across our SCADA radio sites can be reused, but some items may need to be replaced (e.g., the Wes Brown Repeater site antenna and cable, as noted in the answer to question no. 4).
6 | Cutover & redundancy | Are there any restrictions on cutover windows or outage tolerance at repeater sites? | We will need to plan and schedule these times, but there is nothing established at this time.
7 | Cutover & redundancy | Is short-duration service interruption acceptable with prior coordination? | Yes, we just need to plan and schedule these interruptions.
8 | Cybersecurity | The RFP includes detailed cybersecurity questions related to encryption, firmware security, and cloning prevention. Are FIPS 140-2 or 140-3 certifications required, or are they informational/preferred only? | FIPS 140-2 and 140-3 certifications are not required. Thornton is interested in understanding what secure communication standards, if any, proposed radios meet, and will more favorably evaluate solutions that meet recognized secure communication standards.
9 | Cybersecurity | The RFP includes detailed cybersecurity questions related to encryption, firmware security, and cloning prevention. Is AES-256 encryption with digitally signed firmware sufficient to meet Thornton’s expectations? | Vendors shall propose encryption and security configurations for the radios proposed. Thornton will evaluate these proposed encryption and security configurations during proposal evaluations and negotiate with viable vendors, as needed, where Thornton has concerns related to the security of the proposed solution. See Addendum No. 1 to the RFP.
10 | Cybersecurity | Will Thornton require formal third-party cybersecurity certification or audit documentation, or is vendor technical attestation acceptable? | Vendor attestation is acceptable.
11 | Cybersecurity | Is the vendor’s cybersecurity responsibility limited to the radio network, excluding enterprise IT or SCADA server security? | Correct - the scope of this Project, including vendor cybersecurity, is limited to the radios/radio network and does not extend to Thornton's enterprise IT or SCADA server.
12 | IT standards and approvals | Will Thornton provide written IT/network standards (e.g., VLANs, firewall rules, IP addressing) at Project Kickoff? | Yes.
13 | IT standards and approvals | Is the vendor responsible for IT change management approvals, or will Thornton manage those internally? | Thornton will manage IT change management approvals internally. The vendor will be responsible, however, for supplying information needed by Thornton to submit its internal change management requests. Additionally, Thornton will likely require a minimum of a couple of weeks' of lead time to approve change management requests. See Addendum No. 1 to the RFP.
14 | Site access | Will Thornton staff provide escorted access to all sites? | Yes.
15 | Site access | Are any sites restricted to after-hours or weekend access? | No – sites can generally be accessed at any time. There are, however sites located in the neighboring municipality of Northglenn. For these sites, Thornton will coordinate with Northglenn to facilitate the vendor’s access.
16 | Weather/seasonal constraints | Are there any known seasonal blackout periods (e.g., irrigation season, peak demand) during which field work is restricted? | No, there are no set seasonal blackout periods. The work can be completed at any time; the vendor will, however, need to coordinate with Thornton to ensure Thornton has available resources to cover critical sites.
17 | Implementation Phase | Please confirm that final Implementation pricing will be based solely on accepted recommendations. | Correct - final Implementation pricing will be based upon the vendor's recommendations that Thornton accepts, including any negotiations between the parties.
18 | Implementation Phase | Please confirm that Thornton will allow re-baselining of labor and materials if the scope is changed from the placeholder assumption. | Yes, if any of the assumptions the vendor made in its proposal change as a result of the Design Phase, labor and material estimates may be re-baselined and adjusted. That being said, it is important that vendors price the Implementation Phase realistically in their proposals, and Thornton may consider the realism of the pricing proposed for the Implementation Phase in its evaluation of proposals.
19 | PLC interface and compatibility | While PLC replacement or modernization is excluded from the project scope, radio communications necessarily interface with existing PLC hardware and configurations. Please confirm that minor PLC communication parameter adjustments required solely to establish radio communications (e.g., port selection, baud rate, IP addressing) are considered within scope. | Yes, these parameter adjustments to establish radio communications are in-scope.
20 | PLC interface and compatibility | While PLC replacement or modernization is excluded from the project scope, radio communications necessarily interface with existing PLC hardware and configurations. Please confirm that any PLC firmware upgrades, logic changes, hardware replacement, or other PLC modernization required to support new radio equipment will be identified during the Design Phase as recommendations and, if desired by Thornton, procured separately. | Correct - any PLC replacement or modernization is out of scope for this Project and (if pursued) would be procured separately.
21 | FCC licensing/frequency bands | Please confirm that proposers should assume continued operation within Thornton’s existing FCC radio licenses and authorized parameters, and that procurement or modification of FCC licenses or frequency coordination is not included in the project scope unless separately authorized. | Correct - the radio network will continue to operate within our existing licenses. Procuring new or modified FCC licenses, or coordinating for new or additional frequencies, is not within scope.
22 | Permitting | Some installation activities (antenna/mounting changes, grounding modifications, penetrations, or power circuit changes) may, depending on site conditions and AHJ interpretation, require electrical/structural permits or engineered documents. Does Thornton anticipate any permit-triggering work under Tasks 7–10? If so, who is responsible for engineering/design (PE if required), permit applications/coordination, and permit/inspection fees? If permits are not anticipated, please confirm vendors should price work as like-for-like equipment replacement within existing mounting/power arrangements. | Thornton does not anticipate that permits will be required. Vendors should assume like-for-like equipment replacement, with radios being upgraded to the latest MDS Orbit model. We anticipate radios can be replaced within the existing mounting and power arrangements; vendors may assume such in their proposals. Should existing mounting and power arrangements need to be modified to accommodate a new radio, this will be determined and addressed during performance. Per the answer to question no. 5, the scope of this Project includes not only the radios but also radio-related infrastructure, including radio enclosures, grounding/lightning protection, antennas, cabling, and mounts.
23 | Sustainment Phase | Please confirm that the Sustainment Phase (Task 11) is strictly limited to: • Annual inspection • Signal testing • Condition reporting …and excludes repairs, reprogramming, emergency response, or corrective maintenance. | The Sustainment Phase has been expanded to include other tasks; please see Addendum No. 1 to the RFP.
24 | Sustainment Phase | If issues are identified during sustainment inspections, will corrective actions be procured under separate purchase orders? | No - please see Addendum No. 1 to the RFP, which has modified the tasks in the Sustainment phase. The Sustainment phase now includes Task 15, which is for the repair, replacement, or reconfiguration of radios and radio-related infrastructure (as well as providing RF consulting services).
25 | Hardware | In the event of manufacturer supply constraints: will Thornton consider functionally equivalent radio models, subject to prior written approval? | Yes, although we expect the vendor will verify the availability of recommended radios as part of the recommendations furnished to Thornton in Task 6. If manufacturer supply constraints change the radio models proposed under Task 6 relative to what the vendor included in its original proposal, that is acceptable, although functionally equivalent equipment will need to adhere to the same IT security specifications as the originally-proposed equipment.
26 | Training | Please confirm that training requirements are limited to operator-level installation/uninstallation and programming, as stated in Task 10. | This is correct.
27 | Contracting approach | Is Thorton open to separating engineering consulting services from vendor equipment sale and install? | We appreciate this feedback. After reviewing our contracting approach and market offerings, we've decided to maintain the current approach of awarding the full requirement to a single vendor on a single contract. That being said, a vendor may propose to subcontract a portion of the work to another entity if needed to meet Thornton's full requirement.
28 | Pre-proposal conference | Could you please share the presentation? | The Pre-Proposal Conference slide deck is attached to Addendum No. 1. Please note, however, that the changes made to the RFP in Addendum No. 1 are not reflected in this slide deck.
29 | Hardware | Does Thornton desire to use the same manufacturer for new radios? | Yes, we desire to use the same manufacturer as our current radios, just with upgraded/up-to-date models. See RFP Addendum No. 1.
30 | Bonding/insurance | Is a bid bond, payment bond, or performance bond required for this proposal? | No.
31 | FCC licensing/frequency bands | Are FCC licenses already in place, or is the vendor expected to modify or re-license frequencies? | Please see the answer to question 21.
32 | Site access | Will vendor personnel be required to be escorted by Thornton personnel to radio sites during the Implementation phase? | Yes, we anticipate that vendor personnel will require escorts to most sites. Thornton will make available its personnel to accompany the vendor on all of its site visits.
33 | Existing radio documentation | Will Thorton have radio data logs available for review? Or prior RF PM services to support system evaluation? | No, we do not anticipate having radio data logs for review, and there are no preventative maintenance service records on-hand.
34 | Tax exemption status | Can Thornton provide a tax exemption certificate? | Yes - this is available upon request by email to Joshua.Houston@thorntonco.gov.
35 | Project goals | Beyond replacing aging radios, what measurable outcomes define success for Thornton (e.g., reduced alarms, improved polling consistency, enhanced diagnostics, cut over logistics)? | Optimizing signal strength at each site to ensure system reliability and resilience is a key goal.
36 | Permitting | Will permitting be required? | Please see the answer to question 22.
37 | Coordination with other vendors | What kind of collaboration must be done with other vendors for SCADA upgrade and automation projects? In developing our price proposal, should we specify hours for that work? Or labor rates? | We've revised the RFP to characterize the interaction with other vendors as coordination versus collaboration. We do not anticipate any collaboration with other vendors will be required (e.g., co-producing work products or outcomes). Potential coordination issues include coordinating when work can be performed at remote sites to ensure the work does not conflict with another vendor's SCADA project. Thornton will assist with this coordination, which we do not anticipate requiring significant time or effort on behalf of the vendor. See RFP Addendum No. 1.
38 | PLC interface and compatibility | Will radio connectivity be ethernet or do we have to assume serial on some of the older PLC's? | Vendors may assume serial on a majority of our PLCs.
39 | Communication protocols | Do all Remote Terminal Units (RTUs) communicate with the SCADA system using the same protocol, or are multiple protocols in use? Please specify the protocols, as this will affect the radio communication requirements. | Our RTUs communicate using Modbus over both serial and Ethernet connections. The serial connections use RS-232, and the Ethernet connections use TCP/IP.
40 | Communication protocols | Are terminal servers used to convert serial RTU communications to Ethernet/IP? | Yes. Serial RTU communications are converted to Ethernet/IP using a serial-to-Ethernet gateway located at the SCADA polling master.
41 | Repeater locations | Do any of your radio sites act as store and forward sites? | All of our radio sites communicate through the three repeater locations. The repeaters collect data from the remote sites and immediately re-transmit it to the water treatment plants.
42 | Project budget | What is the estimate for this project? | We are not publishing a budget or estimate for this Project.
43 | Proposal evaluation criteria | Do you have evaluation criteria for this project? | See changes to the RFP in Addendum No. 1.
44 | Network architecture | Could you share the network/radio architecture? | Thornton has provided access to publicly-viewable SCADA-related GIS data. This is the only information about the network we intend to publish with the RFP.
45 | Cybersecurity | What is the scope of cybersecurity? Assessment or other tasks in phases? | Generally, our IT team will need to review the technical specifications of the proposed solution to better understand available options and evaluate the offeror's proposed security configurations. After proposal evaluations, Thornton would intend to negotiate with viable vendors, as needed, where Thornton has concerns related to the security of the proposed solution.
46 | Redundancy | Master / Access Point Redundancy Scope. The site inventory provided lists three repeaters for redundancy but does not identify or enumerate the existing Master or Access Point radios serving the listed remote sites. Are all existing Master and Access Point radios (including those serving the MDS SD-series, 4710, TransNet, TransNext, iNET, and 9810 networks) included in the scope of replacement and redundancy, or is redundancy only required for the three listed repeater locations? | Yes, all existing master and access point radios are included in the scope of replacement. Thornton requires redundancy (spare radios) at the three repeater sites, meaning to have that repeater on the shelf and ready to go, as well as a total of four spare radios for the remote sites (two for the 450 MHz band, and two for the 900 MHz band).
47 | Cybersecurity | Security Policy for Legacy SAF ISM Networks (TransNet / TransNext). Several sites in the inventory remain on MDS TransNet, TransNext ISM radio systems, which do not provide the same encryption, authentication, and device-level security controls as the MDS Orbit platform. Is the City’s intent for these sites to remain on their existing ISM platforms, or to be migrated to MDS Orbit ISM radios to align with the security posture of the licensed Orbit network? | The intent is for those sites to to be migrated to MDS Orbit ISM radios to align with the security posture of the licensed Orbit network.
48 | Pending Northglenn sites | Definition of “Pending” Sites. Multiple sites in the inventory are listed as “Pending” including Fox Run LS, Northglenn PS A, Prose Farm PRV and East Cooley. Are these sites included in the scope of this RFP, and if so, what radio model, frequency band, and backhaul path are currently in use at each of these locations? | Yes, these sites (which require Thornton to coordinate access with the neighboring municipality of Northglenn or other entities) are within scope of the RFP. We have added the radio models for each site to the RFP (namely Appendicies Nos. 1 and 2) but other information on these sites is pending and will be provided to the awarded vendor. Please see Addendum No. 1 to the RFP.
49 | FCC licensing/frequency bands | Spectrum and Architecture Authority. The existing system uses a mix of licensed and unlicensed spectrum (450–520 MHz, 896–960 MHz, and 902–928 MHz ISM) and includes repeater, multi-hop, and store-and-forward radio paths. Is the City expecting these frequency bands and RF paths to be preserved as they exist today, or are bidders authorized to modify spectrum usage, RF paths, and site interconnections as part of their proposed solution? | We expect the frequency bands and RF paths to be maintained as they are today; however, we are open to the awarded vendor's recommendations. The use of 450 MHz and 900 MHz bands will not change, however.
50 | RAD-900-IFS and RAD-2400-IFS radio platforms | RAD Radio Upgrade Strategy. The existing SCADA network includes RAD-900-IFS and RAD-2400-IFS radio platforms that are currently part of the City’s operational radio infrastructure. What is the City’s intended upgrade path for the RAD-900-IFS and RAD-2400-IFS radios — should these platforms remain in long-term service as part of the SCADA communications network, or is the City planning a phased or full replacement of these radios as part of this project's migration strategy? | These radios will stay as-is and are not part of the upgrade. Please see Addendum No. 1 to the RFP.
51 | Bonding/insurance | B.13 INSURANCE. Can the commercial general liability, minimum limit of $2,000,000 per occurrence, be covered by an Umbrella policy? | The required commercial general liability insurance minimum limits may be satisfied by a combination of commercial general liability and umbrella policies, provided (a) the umbrella policy follows the same (or broader) coverage terms as the commercial general liability policy; (b) Thornton, its officers, agents, and employees are named as additional insureds on the umbrella policy; and (c) the combination of the commercial general liability and umbrella policies meet or exceed each of the limits provided in the RFP. Please see Addendum No. 1 to the RFP.
52 | Signal strength | What sites have Weak Signals? | All sites have at least an 80% success. Failures are only a few seconds in duration, which have not been concerning.
53 | Pre-proposal conference | Who Attended the Per Proposal bid? | The following firms attended the pre-proposal conference: ADCOMM Engineering LLC BearCom Castle Rock Microwave CC&E Engineers Ceragon Global Data Specialists KNS Communications SOAP Engineering, LLC
54 | Sustainment Phase | What level of the Service agreement are you looking for: 8/5 of 24 hour? | All tasks in the Sustainment Phase require support only within the vendor's normal business hours. 24-hour support is not required. Please see Addendum No. 1 to the RFP.
55 | FCC licensing/frequency bands | What Actual frequencies are you currently on and what are you looking for the New System? | We currently use 450 MHz and 900 MHz and will remain on these frequency bands.
56 | Field review of remote sites | 6. What exactly are the deliverables for the "survey" portion. Do they expect line and antenna sweeps, and for us to log into the radios and go through the GUI? If so, are they prepared for the sites to go down during that time? | Yes, line and antenna sweeps are expected. We are prepared for sites to go down during the vendor's inspection and review of the site; we will simply need to coordinate with Thornton's operational staff.
57 | Staff training | For task 10. Please confirm the required number of training hours to be provided to Thornton staff for the installation and programming of the new radio equipment, including the expected training format (classroom, hands-on, or hybrid). | We anticipate that less than one day/8 hours of training will be needed. We have no hard requirement on training length or format; vendors are free to propose how they would meet the training task.
58 | Sustainment Phase | For task 11. Please confirm whether the vendor is expected to perform the identified repairs and equipment replacements, or if this scope will be handled separately by Thornton or a third party. Additionally, please clarify how any required repairs or equipment replacements will be commercially addressed (included in scope, change order, or separate contract). | Please see Addendum No. 1 to the RFP, which makes several changes to the Sustainment Phase.
59 | Pending Northglenn sites | In Table 3, Column E, please indicate the existing radio model for the items marked as ‘Pending.’ | Please see the response to question # 48.
60 | Duplicate WGL 2 site | In Table 3, a duplicate site has been identified: WGL2, resulting in a total of 63 sites. Please clarify | This has been corrected. The duplicate WGL 2 site is actually WGL 3. They are co-located and therefore share the same lat/log. Please see Addendum No. 1 to the RFP.
61 | Coordination with other vendors | What kind of collaboration must be done with other vendors for SCADA upgrade and automation projects? In the costing document, should we specify a quantity of hours or rates for that? | Please see the response to question # 37.
62 | PLC interface and compatibility | What will be the newly upgraded SCADA/PLCs? | The PLCs are not being upgraded at this time.
63 | Communication protocols | What kind of communication protocols, security and other requirements must a new radio system and should have? | The communication protocols will remain the same; please refer to the responses to question # 39 and # 40. For security requirements, please refer to the response to question # 9.
64 | Acceptance criteria | Do you have a specific acceptance criterion for project success? | Vendors are asked to propose acceptance criteria in section C.2(B)(5). Thornton does not have any specific criteria beyond what has been included in the RFP.
65 | Warranty | Do you need a specific warranty duration on equipment? | We are requesting only standard commercial warranties that are offered for the proposed equipment.
66 | Project schedule | Do you have a preferred timeline (duration) of phases to complete the project? | Vendors are asked to provide a proposed project schedule in section C.2(B)(4). The only requirement we have is that the Implementation Phase must be completed no later than December 31, 2026. Vendors are free to propose the duration of phases leading up to the milestone for the completion of Implementation.
67 | Site access | Will you have personnel/mobilization to accompany the contractor to visit and inspect remote sites? Could you assign two people to create two groups and visit sites in a shorter time? | Yes, Thornton staff will accompany the vendor to the remote sites. We do have the capacity to support two separate groups.
68 | FCC licensing/frequency bands | What FCC call signs are applicable to this project? | We are not aware of Thornton being assigned any FCC call signs, as our radios are used for data transmission only. The City of Thornton owns the FCC licenses we use and these can be shared with the awarded vendor.
69 | Topology map | Is there a current radio topology map available showing connectivity paths? | No, we do not have a topology map.
70 | Scope of Work | Which of the statements below are correct? -Pg 5 B.2 SCOPE OF WORK – GENERAL The scope of this project is radio services for sixty-two (62) remote sites and the two (2) water treatment plants. -Pg 6 The vendor will also install upgraded radios for the three (3) repeater sites and provide new redundant radios for each radio at the repeater site locations (Task 8). | Both statements are correct. The universe of this Project is sixty-two (62) remote sites and the two (2) water treatment plants. Within this universe, there is a task (now Task 9) to upgrade the three (3) repeater site radios (the three repeater sites being the 102nd/Zone 5 PS repeater, which is also a remote site, and the repeaters at the two water treatment plants) and provide redundant radios for each of these three repeater sites.
71 | Duplicate WGL 2 site | On the 112-26 Appendix No. 1 Remote SCADA spreadsheet Line 42 and 43 show redundant WGL2 sites with the same coordinates. Please clarify? | Please see the response to question # 60.
72 | Site naming | There are different naming standards on GIS versus the site spreadsheet. Which one should have precedence? | For vendor proposals, please use the naming convention published in the RFP. After award, Thornton will work with the awarded vendor to resolve any conflicts between the RFP naming convention and the names published in the GIS data viewer.
73 | Antennas | Would you have the antenna heights for each location? | Remote site antennas are generally between 10-20 ft. The antenna at the Thornton Water Treatment Plant (TWTP) and at the 102nd/Zone 5 PS/900 Repeater are each 120 ft. The antenna at the Wes Brown Water Treatment Plant (WBTP) is 20 ft.
74 | FCC licensing/frequency bands | There currently is a mix of licensed and unlicensed solutions. Is this acceptable for the future? | Yes; Thornton anticipates continuing with a mix of licensed and unlicensed solutions.
75 | Network architecture | What type a model number Master/Base Stations are located at the head ends? | MDS 4790 (450 MHz), MDS 9790 (900 MHz), and MPRS (900 MHz).
76 | Radio management system software | Are you looking for or do you have a Management System in place? | We do not currently use radio management system software (i.e., software to configure, monitor, control, and maintain the radio network), and such a system is not within scope of this project, as we do not presently have plans to acquire such a system.
77 | FCC licensing/frequency bands | Where are you in the 900Mhz: License or unlicensed? | Licensed.